## FY11-12
CEDAR RAPIDS WATER DEPARTMENT
FINISHED WATER ANALYSIS SUMMARY
J AVENUE WATER PLANT
FY 11-12
[5 empty] | FINISHED WATER HARDNESS LEVELS |  |  |  | ALKALINITY |  | Total |  | Coliform | Sodium
FY 11-12 | p H | Temperature |  |  | mg/L (as CaCO3) |  |  |  | mg/L (as CaCO3) |  | Chlorine | Fluoride | Bacteria
Month | S.U.'s | Degrees F | Total | Calcium |  | Magnesium | Non-Carb. | Total |  | Phenolpht. | mg/L | mg/L | CFU/100 mL | mg/L
2011-07-01 | 8.19 | 66.5 | 118 | 60 |  | 58 | 54 | 65 |  | 0 | 3.24 | 0.66 | Absent | 9.1
2011-08-01 | 8.27 | 70.1 | 106 | 55 |  | 52 | 47 | 59 |  | 0 | 3.2 | 0.7 | Absent | 9.3
2011-09-11 | 8.26 | 68 | 102 | 55 |  | 46 | 44 | 58 |  | 0 | 3.2 | 0.68 | Absent | 11.3
2011-10-11 | 8.21 | 65 | 105 | 52 |  | 52 | 44 | 60 |  | 0 | 3 | 0.64 | Absent | 13.1
2011-11-11 | 8.18 | 60.9 | 110 | 52 |  | 55 | 43 | 67 |  | 0 | 3.3 | 0.63 | Absent | 14.8
2011-12-11 | 8.13 | 60.2 | 123 | 56 |  | 67 | 51 | 72 |  | 0 | 3.3 | 0.61 | Absent | 14.7
2012-01-12 | 8.13 | 56.5 | 136 | 61 |  | 74 | 58 | 78 |  | 0 | 3.4 | 0.64 | Absent | 14.5
2012-02-12 | 8.11 | 52.1 | 143 | 62 |  | 81 | 64 | 79 |  | 0 | 3.36 | 0.64 | Absent | 15.2
2012-03-12 | 8.12 | 49.4 | 139 | 59 |  | 80 | 61 | 79 |  | 0 | 3.4 | 0.64 | Absent | 15.4
2012-04-12 | 8.21 | 50.7 | 132 | 59 |  | 73 | 51 | 81 |  | 0 | 3.3 | 0.62 | Absent | 14.9
2012-05-12 | 8.22 | 55.6 | 127 | 59 |  | 69 | 47 | 79 |  | 0 | 3.2 | 0.67 | Absent | 13.8
2012-06-12 | 8.2 | 61.3 | 115 | 54 |  | 61 | 45 | 70 |  | 0 | 3.2 | 0.61 | Absent | 12.5
FY AVG | 8.1855 | 59.0727 | 121.6364 | 56.7273 |  | 64.5455 | 50.4545 | 71.0909 |  | 0 | 3.26 | 0.64364
MAXIMUM | 8.27 | 70.1 | 143 | 62 |  | 81 | 64 | 81 |  | 0 | 3.4 | 0.7
MINIMUM | 8.11 | 49.4 | 102 | 52 |  | 46 | 43 | 58 |  | 0 | 3 | 0.61
FY 11-12 | Nitrate | Nitrite | Ammonia | O-Phosphate |  | Chloride | Sulfate | Iron |  | Conductivity | Turbidity | Dissolved
Month | mg/L (asN) | mg/L (asN) | mg/L (asN) | mg/L (as PO4) |  | mg/L | mg/L as(SO4) | mg/L |  | µmhos/Cm | NTU's | Solids
2011-07-01 | 4.94 | 0.04 | 0.74 | 0.65 |  | 24.5 | 25.9 | ND |  | 285 | 0.04 | 189
2011-08-01 | 2.21 | 0.02 | 0.69 | 0.65 |  | 25.8 | 27.4 | ND |  | 261 | 0.03 | 182
2011-09-11 | 0.79 | 0.03 | 0.68 | 0.65 |  | 28.7 | 28.2 | ND |  | 260 | 0.03 | 156
2011-10-11 | 0.42 | ND | 0.68 | 0.65 |  | 30.9 | 27 | ND |  | 270 | 0.03 | 155
2011-11-11 | 0.4 | ND | 0.67 | 0.65 |  | 32.8 | 29 | ND |  | 289 | 0.04 | 175
2011-12-11 | 1.08 | ND | 0.78 | 0.65 |  | 33.2 | 33.1 | ND |  | 311 | 0.03 | 183
2012-01-12 | 1.47 | 0 | 0.8 | 0.65 |  | 33.7 | 36.6 | 0 |  | 333 | 0.04 | 205
2012-02-12 | 1.98 | 0 | 0.79 | 0.65 |  | 36 | 39.3 | ND |  | 349 | 0.03 | 193
2012-03-12 | 1.87 | 0.01 | 0.81 | 0.64 |  | 36 | 38 | 0 |  | 340 | 0.03 | 179
2012-04-12 | 0.95 | 0.01 | 0.76 | 0.66 |  | 33.9 | 33.8 | 0 |  | 323 | 0.03 | 210
2012-05-12 | 1.07 | 0 | 0.85 | 0.65 |  | 32.2 | 29.7 | 0 |  | 333 | 0.04 | 187
2012-06-12 | 1.11 | 0.01 | 0.78 | 0.65 |  | 31.7 | 27.6 | 0 |  | 314 | 0.04 | 170
FY AVG | 1.2136 | <0.02 | 0.75364 | 0.65 |  | 32.2636 | 31.7909 | ND |  | 307.5455 | 0.033636 | 181.3636
MAXIMUM | 2.21 | <0.02 | 0.85 | 0.66 |  | 36 | 39.3 | ND |  | 349 | 0.04 | 210
MINIMUM | 0.4 | <0.02 | 0.67 | 0.64 |  | 25.8 | 27 | ND |  | 260 | 0.03 | 155
CEDAR RAPIDS WATER DEPARTMENT
FINISHED WATER ANALYSIS SUMMARY
NW WATER PLANT
FY 11-12
[5 empty] | FINISHED WATER HARDNESS LEVELS |  |  |  | ALKALINITY |  | Total |  | Coliform | Sodium
FY 11-12 | p H | Temperature |  |  | mg/L (as CaCO3) |  |  |  | mg/L (as CaCO3) |  | Chlorine | Fluoride | Bacteria
Month | S.U.'s | Degrees F | Total | Calcium |  | Magnesium | Non-Carb. | Total |  | Phenolpht. | mg/L | mg/l | CFU/100 mL | mg/L
2011-07-01 | 8.27 | 64.9 | 106 | 51 |  | 54 | 58 | 48 |  | 0 | 3.33 | 0.64 | Absent | 8.25
2011-08-01 | 8.23 | 70.6 | 97 | 48 |  | 49 | 51 | 46 |  | 0 | 3.3 | 0.75 | Absent | 8.6
2011-09-11 | 8.23 | 69.3 | 95 | 46 |  | 48 | 48 | 46 |  | 0 | 3.2 | 0.73 | Absent | 10.8
2011-10-11 | 8.21 | 65.1 | 100 | 46 |  | 53 | 48 | 52 |  | 0 | 3.3 | 0.67 | Absent | 12.5
2011-11-11 | 8.24 | 60.5 | 103 | 45 |  | 58 | 48 | 55 |  | 0 | 3.3 | 0.57 | Absent | 14.1
2011-12-11 | 8.24 | 55 | 114 | 47 |  | 68 | 56 | 58 |  | 0 | 3.26 | 0.66 | Absent | 13.7
2012-01-12 | 8.2 | 49.2 | 125 | 49 |  | 78 | 67 | 61 |  | 0 | 3.4 | 0.65 | Absent | 13.3
2012-02-12 | 8.24 | 46.1 | 129 | 50 |  | 79 | 69 | 60 |  | 0 | 3.46 | 0.51 | Absent | 14.3
2012-03-12 | 8.24 | 45 | 132 | 48 |  | 84 | 66 | 66 |  | 0 | 3.5 | 0.65 | Absent | 14.9
2012-04-12 | 8.24 | 50.7 | 117 | 43 |  | 74 | 58 | 59 |  | 0 | 3.5 | 0.64 | Absent | 14.2
2012-05-12 | 8.2 | 56 | 116 | 48 |  | 68 | 63 | 53 |  | 0 | 3.4 | 0.62 | Absent | 12.5
2012-06-12 | 8.15 | 63 | 106 | 47 |  | 59 | 60 | 46 |  | 0 | 3.4 | 0.63 | Absent | 11.3
FY AVG | 8.22 | 57.3182 | 112.1818 | 47 |  | 65.2727 | 57.6364 | 54.7273 |  | 0 | 3.3655 | 0.64364
MAXIMUM | 8.24 | 70.6 | 132 | 50 |  | 84 | 69 | 66 |  | 0 | 3.5 | 0.75
MINIMUM | 8.15 | 45 | 95 | 43 |  | 48 | 48 | 46 |  | 0 | 3.2 | 0.51
FY 11-12 | Nitrate | Nitrite | Ammonia | O-Phosphate |  | Chloride | Sulfate | Iron |  | Conductivity | Turbidity | Dissolved
Month | mg/L (asN) | mg/L (asN) | mg/L (asN) | mg/L (as PO4) |  | mg/L | mg/L as(SO4) | mg/L |  | µmhos/Cm | NTU's | Solids
2011-07-01 | 6.13 | 0.05 | 0.7 | 0.71 |  | 23.4 | 24.4 | ND |  | 260 | 0.1 | 194
2011-08-01 | 3.28 | 0.02 | 0.71 | 0.7 |  | 24.4 | 27.3 | ND |  | 242 | 0.09 | 167
2011-09-11 | 1.35 | 0.03 | 0.76 | 0.69 |  | 27.5 | 30.7 | ND |  | 247 | 0.06 | 138
2011-10-11 | 0.87 | ND | 0.79 | 0.66 |  | 29.8 | 31.5 | ND |  | 261 | 0.06 | 149
2011-11-11 | 0.89 | ND | 0.71 | 0.67 |  | 30.7 | 32.8 | ND |  | 273 | 0.05 | 124
2011-12-11 | 2.15 | ND | 0.71 | 0.66 |  | 31.5 | 35.5 | ND |  | 294 | 0.04 | 175
2012-01-12 | 3.49 | 0 | 0.72 | 0.65 |  | 31.6 | 35.9 | 0 |  | 311 | 0.04 | 186
2012-02-12 | 4.15 | 0 | 0.76 | 0.65 |  | 34.9 | 37.4 | ND |  | 323 | 0.03 | 182
2012-03-12 | 4.11 | 0 | 0.8 | 0.65 |  | 35 | 37 | 0 |  | 328 | 0.05 | 180
2012-04-12 | 2.87 | 0 | 0.71 | 0.66 |  | 32.3 | 34.5 | 0 |  | 300 | 0.05 | 218
2012-05-12 | 4.99 | 0 | 0.77 | 0.67 |  | 29.7 | 30.7 | 0 |  | 314 | 0.05 | 171
2012-06-12 | 3.79 | 0.01 | 0.69 | 0.66 |  | 29.5 | 30.2 | 0 |  | 291 | 0.05 | 167
FY AVG | 2.9036 | 0.0075 | 0.73909 | 0.66545 |  | 30.6273 | 33.0455 | 0 |  | 289.4545 | 0.051818 | 168.8182
MAXIMUM | 4.99 | 0.03 | 0.8 | 0.7 |  | 35 | 37.4 | 0 |  | 328 | 0.09 | 218
MINIMUM | 0.87 | 0 | 0.69 | 0.65 |  | 24.4 | 27.3 | 0 |  | 242 | 0.03 | 124
Note: ND = Not Detected; NR = No Result
Note: A= Absent or 0 cfu/100 mL

## FY12-13
CEDAR RAPIDS WATER DEPARTMENT
FINISHED WATER ANALYSIS SUMMARY
J AVENUE WATER PLANT
FY 12-13
[5 empty] | FINISHED WATER HARDNESS LEVELS |  |  |  | ALKALINITY |  | Total |  | Coliform | Sodium
FY 12-13 | p H | Temperature |  |  | mg/L (as CaCO3) |  |  |  | mg/L (as CaCO3) |  | Chlorine | Fluoride | Bacteria
Month | S.U.'s | Degrees F | Total | Calcium |  | Magnesium | Non-Carb. | Total |  | Phenolpht. | mg/L | mg/L | CFU/100 mL | mg/L
2012-07-01 | 8.23 | 66 | 108 | 51 |  | 57 | 37 | 71 |  | 0 | 3.1 | 0.58 | Absent | 12.3
2012-08-01 | 8.21 | 68.3 | 102 | 51 |  | 51 | 32 | 70 |  | 0 | 3.2 | 0.62 | Absent | 14.2
2012-09-11 | 8.24 | 68.4 | 102 | 52 |  | 50 | 35 | 67 |  | 0 | 3.3 | 0.61 | Absent | 16.1
2012-10-11 | 8.22 | 66.7 | 100 | 52 |  | 48 | 35 | 65 |  | 0 | 3.3 | 0.6 | Absent | 17.1
2012-11-11 | 8.24 | 65.7 | 110 | 60 |  | 51 | 36 | 74 |  | 0 | 3.2 | 0.52 | Absent | 18.2
2012-12-11 | 8.2 | 63 | 118 | 59 |  | 59 | 43 | 75 |  | 0 | 3.4 | 0.54 | Absent | 18.1
2013-01-12 | 8.17 | 60.9 | 126 | 62 |  | 64 | 49 | 77 |  | 0 | 3.3 | 0.48 | Absent | 20.2
2013-02-12 | 8.2 | 56.5 | 136 | 67 |  | 70 | 59 | 78 |  | 0 | 3.4 | 0.46 | Absent | 20.7
2013-03-12 | 8.2 | 52.8 | 141 | 71 |  | 70 | 58 | 84 |  | 0 | 3.3 | 0.46 | Absent | 18.6
2013-04-12 | 8.19 | 50.1 | 129 | 71 |  | 59 | 54 | 75 |  | 0 | 3.2 | 0.53 | Absent | 14.9
2013-05-12 | 8.19 | 52.2 | 134 | 73 |  | 61 | 69 | 64 |  | 0 | 3.3 | 0.61 | Absent | 11.6
2013-06-01 | 8.18 | 59.9 | 120 | 64 |  | 56 | 64 | 56 |  | 0 | 3.2 | 0.56 | Absent | 9.96
FY AVG | 8.2036 | 60.4091 | 119.8182 | 62 |  | 58.0909 | 48.5455 | 71.3636 |  | 0 | 3.2818 | 0.54455
MAXIMUM | 8.24 | 68.4 | 141 | 73 |  | 70 | 69 | 84 |  | 0 | 3.4 | 0.62
MINIMUM | 8.17 | 50.1 | 100 | 51 |  | 48 | 32 | 56 |  | 0 | 3.2 | 0.46
FY 12-13 | Nitrate | Nitrite | Ammonia | O-Phosphate |  | Chloride | Sulfate | Iron |  | Conductivity | Turbidity | Dissolved
Month | mg/L (asN) | mg/L (asN) | mg/L (asN) | mg/L (as PO4) |  | mg/L | mg/L as(SO4) | mg/L |  | µmhos/Cm | NTU's | Solids
2012-07-01 | 0.35 | 0.03 | 0.9 | 0.67 |  | 32.6 | 23.9 | 0 |  | 302 | 0.04 | 170
2012-08-01 | 0.21 | 0.03 | 0.88 | 0.66 |  | 34.2 | 18.2 | 0 |  | 293 | 0.04 | 149
2012-09-11 | 0.19 | 0.03 | 0.86 | 0.65 |  | 35.8 | 19.1 | 0 |  | 296 | 0.04 | 158
2012-10-11 | 0.23 | 0.04 | 0.8 | 0.65 |  | 37.5 | 20 | 0 |  | 301 | 0.04 | 158
2012-11-11 | 0.28 | 0.03 | 0.85 | 0.66 |  | 38.8 | 21.2 | 0 |  | 323 | 0.04 | 175
2012-12-11 | 0.25 | 0.02 | 0.8 | 0.65 |  | 39.3 | 29 | 0.01 |  | 338 | 0.04 | 203
2013-01-12 | 0.27 | 0.03 | 0.88 | 0.64 |  | 41.1 | 32.6 | 0 |  | 356 | 0.04 | 204
2013-02-12 | 0.38 | 0.03 | 1.03 | 0.65 |  | 45.2 | 40.3 | 0 |  | 385 | 0.04 | 242
2013-03-12 | 0.69 | 0.04 | 1.09 | 0.65 |  | 42.8 | 39.1 | 0 |  | 389 | 0.04 | 233
2013-04-12 | 1.48 | 0.02 | 0.76 | 0.68 |  | 34.8 | 34 | 0 |  | 350 | 0.05 | 214
2013-05-12 | 5.03 | 0.04 | 0.85 | 0.67 |  | 31.8 | 32.8 | 0 |  | 350 | 0.05 | 204
2013-06-12 | 5.67 | 0.04 | 0.78 | 0.66 |  | 28.3 | 27.6 | 0 |  | 317 | 0.05 | 194
FY AVG | 1.3345 | <0.02 | 0.87091 | 0.65636 |  | 37.2364 | 28.5364 | ND |  | 336.1818 | 0.042727 | 194
MAXIMUM | 5.67 | <0.02 | 1.09 | 0.68 |  | 45.2 | 40.3 | ND |  | 389 | 0.05 | 242
MINIMUM | 0.19 | <0.02 | 0.76 | 0.64 |  | 28.3 | 18.2 | ND |  | 293 | 0.04 | 149
CEDAR RAPIDS WATER DEPARTMENT
FINISHED WATER ANALYSIS SUMMARY
NW WATER PLANT
FY 12-13
[5 empty] | FINISHED WATER HARDNESS LEVELS |  |  |  | ALKALINITY |  | Total |  | Coliform | Sodium
FY 12-13 | p H | Temperature |  |  | mg/L (as CaCO3) |  |  |  | mg/L (as CaCO3) |  | Chlorine | Fluoride | Bacteria
Month | S.U.'s | Degrees F | Total | Calcium |  | Magnesium | Non-Carb. | Total |  | Phenolpht. | mg/L | mg/l | CFU/100 mL | mg/L
2012-07-01 | 8.16 | 70.1 | 94 | 42 |  | 52 | 48 | 46 |  | 0 | 3.3 | 0.63 | Absent | 11.3
2012-08-01 | 8.19 | 70.8 | 93 | 41 |  | 52 | 42 | 50 |  | 0 | 3.3 | 0.67 | Absent | 14.3
2012-09-11 | 8.23 | 68.9 | 95 | 43 |  | 53 | 44 | 52 |  | 0 | 3.3 | 0.67 | Absent | 16.3
2012-10-11 | 8.2 | 64.7 | 103 | 44 |  | 60 | 46 | 58 |  | 0 | 3.3 | 0.65 | Absent | 17.1
2012-11-11 | 8.21 | 60.7 | 109 | 49 |  | 61 | 51 | 59 |  | 0 | 3.4 | 0.61 | Absent | 18.3
2012-12-11 | 8.17 | 55.3 | 114 | 46 |  | 68 | 57 | 57 |  | 0 | 3.3 | 0.58 | Absent | 17.1
2013-01-12 | 8.18 | 53.7 | 118 | 44 |  | 73 | 62 | 56 |  | 0 | 3.2 | 0.54 | Absent | 20.3
2013-02-12 | 8.15 | 49.9 | 124 | 49 |  | 75 | 70 | 54 |  | 0 | 3.4 | 0.5 | Absent | 21.7
2013-03-12 | 8.15 | 48.8 | 122 | 47 |  | 75 | 67 | 55 |  | 0 | 3.4 | 0.54 | Absent | 18.5
2013-04-12 | 8.15 | 47.1 | 121 | 52 |  | 69 | 64 | 57 |  | 0 | 3.4 | 0.55 | Absent | 16.1
2013-05-12 | 8.09 | 50.1 | 121 | 54 |  | 66 | 75 | 46 |  | 0 | 3.4 | 0.56 | Absent | 11.7
2013-06-12 | 8.22 | 56.4 | 111 | 48 |  | 63 | 66 | 45 |  | 0 | 3.4 | 0.56 | Absent | 9.5
FY AVG | 8.1764 | 56.9455 | 111.9091 | 47 |  | 65 | 58.5455 | 53.5455 |  | 0 | 3.3455 | 0.58455
MAXIMUM | 8.23 | 70.8 | 124 | 54 |  | 75 | 75 | 59 |  | 0 | 3.4 | 0.67
MINIMUM | 8.09 | 47.1 | 93 | 41 |  | 52 | 42 | 45 |  | 0 | 3.2 | 0.5
FY 12-13 | Nitrate | Nitrite | Ammonia | O-Phosphate |  | Chloride | Sulfate | Iron |  | Conductivity | Turbidity | Dissolved
Month | mg/L (asN) | mg/L (asN) | mg/L (asN) | mg/L (as PO4) |  | mg/L | mg/L as(SO4) | mg/L |  | µmhos/Cm | NTU's | Solids
2012-07-01 | 1.15 | 0.03 | 0.83 | 0.67 |  | 30.8 | 29.8 | 0 |  | 273 | 0.06 | 155
2012-08-01 | 0.69 | 0.04 | 0.87 | 0.69 |  | 33 | 27.2 | 0 |  | 277 | 0.06 | 142
2012-09-11 | 0.46 | 0.03 | 0.84 | 0.68 |  | 34.8 | 28.6 | 0 |  | 288 | 0.05 | 151
2012-10-11 | 0.4 | 0.04 | 0.86 | 0.69 |  | 36.4 | 30.6 | 0 |  | 305 | 0.06 | 151
2012-11-11 | 0.72 | 0.05 | 0.81 | 0.69 |  | 37.8 | 34.8 | 0 |  | 320 | 0.05 | 176
2012-12-11 | 0.88 | 0.03 | 0.79 | 0.7 |  | 39.5 | 36 | 0 |  | 330 | 0.05 | 206
2013-01-12 | 1.06 | 0.03 | 0.83 | 0.66 |  | 40.4 | 42.4 | 0.01 |  | 344 | 0.05 | 200
2013-02-12 | 2.03 | 0.03 | 0.89 | 0.66 |  | 44.6 | 46.3 | 0 |  | 367 | 0.05 | 220
2013-03-12 | 2.26 | 0.03 | 0.8 | 0.66 |  | 39.1 | 44.8 | 0 |  | 355 | 0.06 | 207
2013-04-12 | 2.53 | 0.03 | 0.88 | 0.7 |  | 34.6 | 41.2 | 0 |  | 338 | 0.05 | 198
2013-05-12 | 6.37 | 0.03 | 0.78 | 0.66 |  | 31 | 35.6 | 0 |  | 327 | 0.06 | 187
2013-06-12 | 6.64 | 0.03 | 0.73 | 0.67 |  | 26 | 28.3 | 0 |  | 294 | 0.07 | 173
FY AVG | 2.1855 | 0.033636 | 0.82545 | 0.67818 |  | 36.1091 | 35.9818 | 0.00090909 |  | 322.2727 | 0.055455 | 182.8182
MAXIMUM | 6.64 | 0.05 | 0.89 | 0.7 |  | 44.6 | 46.3 | 0.01 |  | 367 | 0.07 | 220
MINIMUM | 0.4 | 0.03 | 0.73 | 0.66 |  | 26 | 27.2 | 0 |  | 277 | 0.05 | 142
Note: ND = Not Detected; NR = No Result
Note: A= Absent or 0 cfu/100 mL

## CY2010
CEDAR RAPIDS WATER DEPARTMENT
FINISHED WATER ANALYSIS SUMMARY
J AVENUE WATER PLANT
CY 2010
[5 empty] | FINISHED WATER HARDNESS LEVELS |  |  |  | ALKALINITY |  | Total |  | Coliform | Sodium
YEAR | p H | Temperature |  |  | mg/L (as CaCO3) |  |  |  | mg/L (as CaCO3) |  | Chlorine | Fluoride | Bacteria
2010 | S.U.'s | Degrees F | Total | Calcium |  | Magnesium | Non-Carb. | Total |  | Phenolpht. | mg/L | mg/L | CFU/100 mL | mg/L
2010-01-01 | 8.13 | 53.7 | 131 | 61 |  | 70 | 63 | 68 |  | 0 | 3.4 | 0.91 | Absent | 10.9
2010-02-01 | 8.16 | 52.9 | 134 | 61 |  | 73 | 62 | 72 |  | 0 | 3.1 | 0.97 | Absent | 11.6
2010-03-01 | 8.17 | 50.1 | 128 | 60 |  | 68 | 58 | 70 |  | 0 | 3.3 | 0.95 | Absent | 11
2010-04-01 | 8.25 | 50 | 125 | 60 |  | 65 | 58 | 68 |  | 0 | 3.4 | 0.95 | Absent | 9.8
2010-05-01 | 8.21 | 53.8 | 123 | 57 |  | 66 | 58 | 65 |  | 0 | 3.4 | 0.97 | Absent | 9.8
2010-06-01 | 8.26 | 60.6 | 116 | 55 |  | 61 | 54 | 62 |  | 0 | 3.3 | 0.2 | Absent | 9.3
2010-07-09 | 8.27 | 64.8 | 110 | 55 |  | 55 | 49 | 62 |  | 0 | 3.25 | 0.23 | Absent | 8.39
2010-08-09 | 8.14 | 67.4 | 107 | 54 |  | 53 | 46 | 61 |  | 0 | 3.3 | 0.93 | Absent | 8.8
2010-09-09 | 8.11 | 67.1 | 105 | 55 |  | 50 | 47 | 58 |  | 0 | 3.13 | 0.93 | Absent | 9.9
2010-10-09 | 8.21 | 64.1 | 115 | 60 |  | 56 | 48 | 67 |  | 0 | 3.2 | 1 | Absent | 10.5
2010-11-09 | 8.14 | 61.4 | 124 | 59 |  | 65 | 51 | 72 |  | 0 | 3.3 | 0.93 | Absent | 10.7
2010-12-09 | 8.07 | 57.7 | 132 | 60 |  | 72 | 57 | 75 |  | 0 | 3.3 | 0.95 | Absent | 11.1
CY AVG | 8.1767 | 58.6333 | 120.8333 | 58.0833 |  | 62.8333 | 54.25 | 66.6667 |  | 0 | 3.2817 | 0.82667 | Absent | 10.1492
MAXIMUM | 8.27 | 67.4 | 134 | 61 |  | 73 | 63 | 75 |  | 0 | 3.4 | 1 | 0 | 11.6
MINIMUM | 8.07 | 50 | 105 | 54 |  | 50 | 46 | 58 |  | 0 | 3.1 | 0.2 | 0 | 8.39
YEAR | Nitrate | Nitrite | Ammonia | O-Phosphate |  | Chloride | Sulfate | Iron |  | Conductivity | Turbidity | Dissolved
2010 | mg/L (asN) | mg/L (asN) | mg/L (asN) | mg/L (as PO4) |  | mg/L | mg/L as(SO4) | mg/L |  | µmhos/Cm | NTU's | Solids
2010-01-01 | 3.87 | 0.01 | 0.8 | 0.67 |  | 28 | 30.7 | ND |  | 318 | 0.04 | 187
2010-02-01 | 3.81 | <0.05 | 0.82 | 0.66 |  | 29.7 | 31.6 | ND |  | 327 | 0.03 | 182
2010-03-01 | 3.44 | <0.02 | 0.84 | 0.67 |  | 28 | 30 | ND |  | 313 | 0.03 | 185
2010-04-01 | 4.17 | <0.02 | 0.82 | 0.67 |  | 26 | 27 | ND |  | 301 | 0.04 | 187
2010-05-01 | 3.91 | <0.05 | 0.75 | 0.69 |  | 26.3 | 27.8 | ND |  | 287 | 0.04 | 190
2010-06-01 | 4.44 | 0.04 | 0.72 | 0.71 |  | 25.4 | 26.1 | ND |  | 277 | 0.24 | 152
2010-07-09 | 3.84 | 0.04 | 0.64 | 0.76 |  | 23.5 | 23.6 | ND |  | 260 | 0.1 | 222
2010-08-09 | 3.01 | 0.03 | 0.71 | 0.76 |  | 22.7 | 23.3 | ND |  | 256 | 0.04 | 194
2010-09-09 | 2.02 | 0.01 | 0.66 | 0.74 |  | 25 | 26.4 | ND |  | 258 | 0.04 | 157
2010-10-09 | 2.23 | 0.01 | 0.71 | 0.67 |  | 26 | 28 | ND |  | 276 | 0.03 | 134
2010-11-09 | 2.44 | 0.02 | 0.81 | 0.66 |  | 27.5 | 30.5 | ND |  | 296 | 0.03 | 166
2010-12-09 | 2.76 | 0.03 | 0.78 | 0.66 |  | 28.6 | 31 | ND |  | 314 | 0.03 | 179
CY AVG | 3.3283 | 0.02375 | 0.755 | 0.69333 |  | 26.3917 | 28 | ND |  | 290.25 | 0.0575 | 177.9167
MAXIMUM | 4.44 | 0.04 | 0.84 | 0.76 |  | 29.7 | 31.6 | 0 |  | 327 | 0.24 | 222
MINIMUM | 2.02 | 0.01 | 0.64 | 0.66 |  | 22.7 | 23.3 | 0 |  | 256 | 0.03 | 134
CEDAR RAPIDS WATER DEPARTMENT
FINISHED WATER ANALYSIS SUMMARY
NW WATER PLANT
CY 2010
[5 empty] | FINISHED WATER HARDNESS LEVELS |  |  |  | ALKALINITY |  | Total |  | Coliform | Sodium
YEAR | p H | Temperature |  |  | mg/L (as CaCO3) |  |  |  | mg/L (as CaCO3) |  | Chlorine | Fluoride | Bacteria
2010 | S.U.'s | Degrees F | Total | Calcium |  | Magnesium | Non-Carb. | Total |  | Phenolpht. | mg/L | mg/l | CFU/100 mL | mg/L
2010-01-01 | 8.16 | 49.2 | 123 | 49 |  | 74 | 67 | 56 |  | 0 | 3.4 | 0.92 | Absent | 8.9
2010-02-01 | 8.21 | 44.6 | 126 | 49 |  | 77 | 67 | 59 |  | 0 | 3.42 | 0.95 | Absent | 10.6
2010-03-01 | 8.22 | 43.7 | 122 | 50 |  | 73 | 62 | 60 |  | 0 | 3.5 | 0.93 | Absent | 10
2010-04-01 | 8.18 | 47 | 120 | 55 |  | 65 | 59 | 61 |  | 0 | 3.48 | 0.92 | Absent | 9
2010-05-01 | 8.17 | 52 | 114 | 50 |  | 65 | 59 | 56 |  | 0 | 3.5 | 0.82 | Absent | 9.2
2010-06-01 | 8.18 | 62 | 108 | 48 |  | 60 | 56 | 52 |  | 0 | 3.5 | 0.83 | Absent | 8.5
2010-07-09 | 8.2 | 68.4 | 100 | 47 |  | 53 | 48 | 51 |  | 0 | 3.43 | 0.86 | Absent | 7.69
2010-08-09 | 8.25 | 70.9 | 96 | 47 |  | 49 | 45 | 51 |  | 0 | 3.44 | 0.98 | Absent | 8.2
2010-09-09 | 8.22 | 68.9 | 97 | 49 |  | 49 | 50 | 48 |  | 0 | 3.44 | 0.9 | Absent | 9.5
2010-10-09 | 8.26 | 64.5 | 104 | 48 |  | 56 | 52 | 52 |  | 0 | 3.5 | 0.88 | Absent | 9.8
2010-11-09 | 8.2 | 58.5 | 112 | 48 |  | 64 | 56 | 56 |  | 0 | 3.5 | 0.91 | Absent | 10.1
2010-12-09 | 8.17 | 52.8 | 121 | 48 |  | 73 | 62 | 59 |  | 0 | 3.4 | 0.96 | Absent | 10.1
CY AVG | 8.2017 | 56.875 | 111.9167 | 49 |  | 63.1667 | 56.9167 | 55.0833 |  | 0 | 3.4592 | 0.905 | Absent | 9.2992
MAXIMUM | 8.26 | 70.9 | 126 | 55 |  | 77 | 67 | 61 |  | 0 | 3.5 | 0.98 | 0 | 10.6
MINIMUM | 8.16 | 43.7 | 96 | 47 |  | 49 | 45 | 48 |  | 0 | 3.4 | 0.82 | 0 | 7.69
YEAR | Nitrate | Nitrite | Ammonia | O-Phosphate |  | Chloride | Sulfate | Iron |  | Conductivity | Turbidity | Dissolved
2010 | mg/L (asN) | mg/L (asN) | mg/L (asN) | mg/L (as PO4) |  | mg/L | mg/L as(SO4) | mg/L |  | µmhos/Cm | NTU's | Solids
2010-01-01 | 5.35 | 0.03 | 0.81 | 0.7 |  | 26.3 | 29.7 | ND |  | 299 | 0.05 | 174
2010-02-01 | 5.5 | <0.05 | 0.78 | 0.67 |  | 27.8 | 30.4 | ND |  | 311 | 0.08 | 167
2010-03-01 | 5.2 | <0.05 | 0.78 | 0.64 |  | 26 | 28 | ND |  | 300 | 0.06 | 179
2010-04-01 | 5.31 | <0.02 | 0.87 | 0.61 |  | 25 | 26 | ND |  | 290 | 0.05 | 171
2010-05-01 | 5.01 | 0.01 | 0.8 | 0.6 |  | 24.5 | 26.3 | ND |  | 272 | 0.04 | 187
2010-06-01 | 5.61 | 0.01 | 0.77 | 0.64 |  | 23.5 | 24.5 | ND |  | 262 | 0.04 | 160
2010-07-09 | 4.66 | 0.02 | 0.7 | 0.63 |  | 20.9 | 20.8 | ND |  | 239 | 0.05 | 176
2010-08-09 | 3.63 | 0.03 | 0.77 | 0.68 |  | 21.1 | 21.7 | ND |  | 235 | 0.09 | 182
2010-09-09 | 2.84 | 0.01 | 0.73 | 0.68 |  | 24.2 | 26.5 | ND |  | 245 | 0.08 | 146
2010-10-09 | 3.61 | ND | 0.73 | 0.69 |  | 24 | 27 | ND |  | 257 | 0.08 | 175
2010-11-09 | 3.7 | ND | 0.82 | 0.74 |  | 25.7 | 30.1 | ND |  | 275 | 0.08 | 138
2010-12-09 | 4.42 | 0.03 | 0.76 | 0.73 |  | 26.4 | 29.7 | ND |  | 289 | 0.07 | 181
CY AVG | 4.57 | 0.02 | 0.77667 | 0.6675 |  | 24.6167 | 26.725 | ND |  | 272.8333 | 0.064167 | 169.6667
MAXIMUM | 5.61 | 0.03 | 0.87 | 0.74 |  | 27.8 | 30.4 | 0 |  | 311 | 0.09 | 187
MINIMUM | 2.84 | 0.01 | 0.7 | 0.6 |  | 20.9 | 20.8 | 0 |  | 235 | 0.04 | 138
Note: ND = Not Detected
Note: A= Absent or 0 cfu/100 mL

## CY2011
CEDAR RAPIDS WATER DEPARTMENT
FINISHED WATER ANALYSIS SUMMARY
J AVENUE WATER PLANT
CY 2011
[5 empty] | FINISHED WATER HARDNESS LEVELS |  |  |  | ALKALINITY |  | Total |  | Coliform | Sodium
YEAR | p H | Temperature |  |  | mg/L (as CaCO3) |  |  |  | mg/L (as CaCO3) |  | Chlorine | Fluoride | Bacteria
2011 | S.U.'s | Degrees F | Total | Calcium |  | Magnesium | Non-Carb. | Total |  | Phenolpht. | mg/L | mg/L | CFU/100 mL | mg/L
2011-01-01 | 8.05 | 51.8 | 139 | 62 |  | 76 | 63 | 76 |  | 0 | 3.3 | 0.87 | Absent | 11.5
2011-02-01 | 8.07 | 51.4 | 136 | 63 |  | 73 | 59 | 77 |  | 0 | 3.2 | 0.89 | Absent | 12
2011-03-01 | 8.17 | 48.6 | 131 | 66 |  | 66 | 58 | 74 |  | 0 | 3.3 | 0.65 | Absent | 10.96
2011-04-01 | 8.19 | 51.2 | 132 | 65 |  | 67 | 57 | 75 |  | 0 | 3.3 | 0.52 | Absent | 10.7
2011-05-01 | 8.16 | 53.1 | 130 | 63 |  | 66 | 56 | 73 |  | 0 | 3.4 | 0.58 | Absent | 10.1
2011-06-01 | 8.15 | 59.5 | 125 | 63 |  | 62 | 57 | 68 |  | 0 | 3.2 | 0.62 | Absent | 10.2
2011-07-11 | 8.19 | 66.5 | 118 | 60 |  | 58 | 54 | 65 |  | 0 | 3.24 | 0.66 | Absent | 9.1
2011-08-11 | 8.27 | 70.1 | 106 | 55 |  | 52 | 47 | 59 |  | 0 | 3.2 | 0.7 | Absent | 9.3
2011-09-11 | 8.26 | 68 | 102 | 55 |  | 46 | 44 | 58 |  | 0 | 3.2 | 0.68 | Absent | 11.3
2011-10-11 | 8.21 | 65 | 105 | 52 |  | 52 | 44 | 60 |  | 0 | 3 | 0.64 | Absent | 13.1
2011-11-11 | 8.18 | 60.9 | 110 | 52 |  | 55 | 43 | 67 |  | 0 | 3.3 | 0.63 | Absent | 14.8
2011-12-11 | 8.13 | 60.2 | 123 | 56 |  | 67 | 51 | 72 |  | 0 | 3.3 | 0.61 | Absent | 14.7
CY AVG | 8.1692 | 58.8583 | 121.4167 | 59.3333 |  | 61.6667 | 52.75 | 68.6667 |  | 0 | 3.245 | 0.67083 | #DIV/0! | 11.48
MAXIMUM | 8.27 | 70.1 | 139 | 66 |  | 76 | 63 | 77 |  | 0 | 3.4 | 0.89 | 0 | 14.8
MINIMUM | 8.05 | 48.6 | 102 | 52 |  | 46 | 43 | 58 |  | 0 | 3 | 0.52 | 0 | 9.1
YEAR | Nitrate | Nitrite | Ammonia | O-Phosphate |  | Chloride | Sulfate | Iron |  | Conductivity | Turbidity | Dissolved
2011 | mg/L (asN) | mg/L (asN) | mg/L (asN) | mg/L (as PO4) |  | mg/L | mg/L as(SO4) | mg/L |  | µmhos/Cm | NTU's | Solids
2011-01-01 | 3.77 | ND | 0.78 | 0.65 |  | 30.5 | 31.6 | ND |  | 326 | 0.03 | 206
2011-02-01 | 3.52 | ND | 0.73 | 0.64 |  | 30 | 32.6 | ND |  | 325 | 0.06 | 203
2011-03-01 | 3.89 | ND | 0.72 | 0.63 |  | 27.7 | 29.1 | ND |  | 307 | 0.03 | 187
2011-04-01 | 4.65 | ND | 0.72 | 0.66 |  | 27 | 28 | ND |  | 309 | 0.03 | 215
2011-05-01 | 5.21 | ND | 0.67 | 0.68 |  | 25.8 | 27.3 | ND |  | 307 | 0.05 | 184
2011-06-01 | 5.22 | 0.02 | 0.77 | 0.65 |  | 25.7 | 26.3 | ND |  | 300 | 0.03 | 194
2011-07-11 | 4.94 | 0.04 | 0.74 | 0.65 |  | 24.5 | 25.9 | ND |  | 285 | 0.04 | 189
2011-08-11 | 2.21 | 0.02 | 0.69 | 0.65 |  | 25.8 | 27.4 | ND |  | 261 | 0.03 | 182
2011-09-11 | 0.79 | 0.03 | 0.68 | 0.65 |  | 28.7 | 28.2 | ND |  | 260 | 0.03 | 156
2011-10-11 | 0.42 | ND | 0.68 | 0.65 |  | 30.9 | 27 | ND |  | 270 | 0.03 | 155
2011-11-11 | 0.4 | ND | 0.67 | 0.65 |  | 32.8 | 29 | ND |  | 289 | 0.04 | 175
2011-12-11 | 1.08 | ND | 0.78 | 0.65 |  | 33.2 | 33.1 | ND |  | 311 | 0.03 | 183
CY AVG | 3.0083 | 0.0275 | 0.71917 | 0.65083 |  | 28.55 | 28.7917 | #DIV/0! |  | 295.8333 | 0.035833 | 185.75
MAXIMUM | 5.22 | 0.04 | 0.78 | 0.68 |  | 33.2 | 33.1 | 0 |  | 326 | 0.06 | 215
MINIMUM | 0.4 | 0.02 | 0.67 | 0.63 |  | 24.5 | 25.9 | 0 |  | 260 | 0.03 | 155
CEDAR RAPIDS WATER DEPARTMENT
FINISHED WATER ANALYSIS SUMMARY
NW WATER PLANT
CY 2011
[5 empty] | FINISHED WATER HARDNESS LEVELS |  |  |  | ALKALINITY |  | Total |  | Coliform | Sodium
YEAR | p H | Temperature |  |  | mg/L (as CaCO3) |  |  |  | mg/L (as CaCO3) |  | Chlorine | Fluoride | Bacteria
2011 | S.U.'s | Degrees F | Total | Calcium |  | Magnesium | Non-Carb. | Total |  | Phenolpht. | mg/L | mg/l | CFU/100 mL | mg/L
2011-01-01 | 8.14 | 47.4 | 128 | 49 |  | 79 | 68 | 60 |  | 0 | 3.5 | 0.96 | Absent | 10.6
2011-02-01 | 8.17 | 43.9 | 132 | 53 |  | 79 | 67 | 65 |  | 0 | 3.4 | 0.95 | Absent | 12
2011-03-01 | 8.18 | 42.8 | 127 | 56 |  | 70 | 62 | 65 |  | 0 | 3.5 | 0.72 | Absent | 10.9
2011-04-01 | 8.22 | 44.6 | 122 | 52 |  | 69 | 60 | 62 |  | 0 | 3.5 | 0.67 | Absent | 9.9
2011-05-01 | 8.24 | 50.3 | 117 | 48 |  | 69 | 62 | 55 |  | 0 | 3.5 | 0.64 | Absent | 9.8
2011-06-01 | 8.29 | 57.2 | 110 | 50 |  | 60 | 60 | 50 |  | 0 | 3.4 | 0.65 | Absent | 8.7
2011-07-11 | 8.27 | 64.9 | 106 | 51 |  | 54 | 58 | 48 |  | 0 | 3.33 | 0.64 | Absent | 8.25
2011-08-11 | 8.23 | 70.6 | 97 | 48 |  | 49 | 51 | 46 |  | 0 | 3.3 | 0.75 | Absent | 8.6
2011-09-11 | 8.23 | 69.3 | 95 | 46 |  | 48 | 48 | 46 |  | 0 | 3.2 | 0.73 | Absent | 10.8
2011-10-11 | 8.21 | 65.1 | 100 | 46 |  | 53 | 48 | 52 |  | 0 | 3.3 | 0.67 | Absent | 12.5
2011-11-11 | 8.24 | 60.5 | 103 | 45 |  | 58 | 48 | 55 |  | 0 | 3.3 | 0.57 | Absent | 14.1
2011-12-11 | 8.24 | 55 | 114 | 47 |  | 68 | 56 | 58 |  | 0 | 3.26 | 0.66 | Absent | 13.7
CY AVG | 8.2217 | 55.9667 | 112.5833 | 49.25 |  | 63 | 57.3333 | 55.1667 |  | 0 | 3.3742 | 0.7175 | #DIV/0! | 10.8208
MAXIMUM | 8.29 | 70.6 | 132 | 56 |  | 79 | 68 | 65 |  | 0 | 3.5 | 0.96 | 0 | 14.1
MINIMUM | 8.14 | 42.8 | 95 | 45 |  | 48 | 48 | 46 |  | 0 | 3.2 | 0.57 | 0 | 8.25
YEAR | Nitrate | Nitrite | Ammonia | O-Phosphate |  | Chloride | Sulfate | Iron |  | Conductivity | Turbidity | Dissolved
2011 | mg/L (asN) | mg/L (asN) | mg/L (asN) | mg/L (as PO4) |  | mg/L | mg/L as(SO4) | mg/L |  | µmhos/Cm | NTU's | Solids
2011-01-01 | 5.27 | ND | 0.86 | 0.73 |  | 30.5 | 31.9 | ND |  | 308 | 0.06 | 175
2011-02-01 | 5.25 | ND | 0.89 | 0.71 |  | 30.3 | 33.3 | ND |  | 322 | 0.08 | 201
2011-03-01 | 5.12 | ND | 0.85 | 0.71 |  | 27.6 | 28.4 | ND |  | 300 | 0.05 | 187
2011-04-01 | 5.85 | ND | 0.87 | 0.74 |  | 25 | 26 | ND |  | 290 | 0.05 | 180
2011-05-01 | 6.48 | ND | 0.81 | 0.7 |  | 24.7 | 25.6 | ND |  | 282 | 0.05 | 177
2011-06-01 | 6.37 | 0.02 | 0.7 | 0.69 |  | 23.8 | 24.1 | ND |  | 270 | 0.09 | 185
2011-07-11 | 6.13 | 0.05 | 0.7 | 0.71 |  | 23.4 | 24.4 | ND |  | 260 | 0.1 | 194
2011-08-11 | 3.28 | 0.02 | 0.71 | 0.7 |  | 24.4 | 27.3 | ND |  | 242 | 0.09 | 167
2011-09-11 | 1.35 | 0.03 | 0.76 | 0.69 |  | 27.5 | 30.7 | ND |  | 247 | 0.06 | 138
2011-10-11 | 0.87 | ND | 0.79 | 0.66 |  | 29.8 | 31.5 | ND |  | 261 | 0.06 | 149
2011-11-11 | 0.89 | ND | 0.71 | 0.67 |  | 30.7 | 32.8 | ND |  | 273 | 0.05 | 124
2011-12-11 | 2.15 | ND | 0.71 | 0.66 |  | 31.5 | 35.5 | ND |  | 294 | 0.04 | 175
CY AVG | 4.0842 | 0.03 | 0.78 | 0.6975 |  | 27.4333 | 29.2917 | #DIV/0! |  | 279.0833 | 0.065 | 171
MAXIMUM | 6.48 | 0.05 | 0.89 | 0.74 |  | 31.5 | 35.5 | 0 |  | 322 | 0.1 | 201
MINIMUM | 0.87 | 0.02 | 0.7 | 0.66 |  | 23.4 | 24.1 | 0 |  | 242 | 0.04 | 124
Note: ND = Not Detected
Note: A= Absent or 0 cfu/100 mL

## CY2012
CEDAR RAPIDS WATER DEPARTMENT
FINISHED WATER ANALYSIS SUMMARY
J AVENUE WATER PLANT
CY 2012
[5 empty] | FINISHED WATER HARDNESS LEVELS |  |  |  | ALKALINITY |  | Total |  | Coliform | Sodium
YEAR | p H | Temperature |  |  | mg/L (as CaCO3) |  |  |  | mg/L (as CaCO3) |  | Chlorine | Fluoride | Bacteria
2012 | S.U.'s | Degrees F | Total | Calcium |  | Magnesium | Non-Carb. | Total |  | Phenolpht. | mg/L | mg/L | CFU/100 mL | mg/L
2012-01-01 | 8.13 | 56.5 | 136 | 61 |  | 74 | 58 | 78 |  | 0 | 3.4 | 0.64 | Absent | 14.5
2012-02-01 | 8.11 | 52.1 | 143 | 62 |  | 81 | 64 | 79 |  | 0 | 3.36 | 0.64 | Absent | 15.2
2012-03-01 | 8.12 | 49.4 | 139 | 59 |  | 80 | 61 | 79 |  | 0 | 3.4 | 0.64 | Absent | 15.4
2012-04-01 | 8.21 | 50.7 | 132 | 59 |  | 73 | 51 | 81 |  | 0 | 3.3 | 0.62 | Absent | 14.9
2012-05-12 | 8.22 | 55.6 | 127 | 59 |  | 69 | 47 | 79 |  | 0 | 3.2 | 0.67 | Absent | 13.8
2012-06-01 | 8.2 | 61.3 | 115 | 54 |  | 61 | 45 | 70 |  | 0 | 3.2 | 0.61 | Absent | 12.5
2012-07-01 | 8.23 | 66 | 108 | 51 |  | 57 | 37 | 71 |  | 0 | 3.1 | 0.58 | Absent | 12.3
2012-08-01 | 8.21 | 68.3 | 102 | 51 |  | 51 | 32 | 70 |  | 0 | 3.2 | 0.62 | Absent | 14.1
2012-09-01 | 8.24 | 68.4 | 102 | 52 |  | 50 | 35 | 67 |  | 0 | 3.3 | 0.61 | Absent | 16.1
2012-10-01 | 8.22 | 66.7 | 100 | 52 |  | 48 | 35 | 65 |  | 0 | 3.3 | 0.6 | Absent | 17.1
2012-11-01 | 8.24 | 65.7 | 110 | 60 |  | 51 | 36 | 74 |  | 0 | 3.2 | 0.52 | Absent | 18.2
2012-12-01 | 8.2 | 63 | 118 | 59 |  | 59 | 43 | 75 |  | 0 | 3.4 | 0.54 | Absent | 18.1
CY AVG | 8.1942 | 60.3083 | 119.3333 | 56.5833 |  | 62.8333 | 45.3333 | 74 |  | 0 | 3.28 | 0.6075 | #DIV/0! | 15.1833
MAXIMUM | 8.24 | 68.4 | 143 | 62 |  | 81 | 64 | 81 |  | 0 | 3.4 | 0.67 | 0 | 18.2
MINIMUM | 8.11 | 49.4 | 100 | 51 |  | 48 | 32 | 65 |  | 0 | 3.1 | 0.52 | 0 | 12.3
YEAR | Nitrate | Nitrite | Ammonia | O-Phosphate |  | Chloride | Sulfate | Iron |  | Conductivity | Turbidity | Dissolved
2012 | mg/L (asN) | mg/L (asN) | mg/L (asN) | mg/L (as PO4) |  | mg/L | mg/L as(SO4) | mg/L |  | µmhos/Cm | NTU's | Solids
2012-01-01 | 1.47 | 0 | 0.8 | 0.65 |  | 33.7 | 36.6 | 0 |  | 333 | 0.04 | 205
2012-02-01 | 1.98 | 0 | 0.79 | 0.65 |  | 36 | 39.3 | 0 |  | 349 | 0.03 | 193
2012-03-01 | 1.87 | 0.01 | 0.81 | 0.64 |  | 36 | 38 | 0 |  | 340 | 0.03 | 179
2012-04-01 | 0.95 | 0.01 | 0.76 | 0.66 |  | 33.9 | 33.8 | 0 |  | 323 | 0.03 | 210
2012-05-12 | 1.07 | 0 | 0.85 | 0.65 |  | 32.2 | 29.7 | 0 |  | 333 | 0.04 | 187
2012-06-01 | 1.11 | 0.01 | 0.78 | 0.65 |  | 31.7 | 27.6 | 0 |  | 314 | 0.04 | 170
2012-07-01 | 0.35 | 0.03 | 0.9 | 0.67 |  | 32.6 | 23.9 | 0 |  | 302 | 0.04 | 170
2012-08-01 | 0.21 | 0.03 | 0.88 | 0.66 |  | 34.2 | 18.2 | 0 |  | 293 | 0.04 | 149
2012-09-01 | 0.19 | 0.03 | 0.86 | 0.65 |  | 35.8 | 19.1 | 0 |  | 296 | 0.04 | 158
2012-10-01 | 0.23 | 0.04 | 0.8 | 0.65 |  | 37.5 | 20 | 0 |  | 301 | 0.04 | 158
2012-11-01 | 0.28 | 0.03 | 0.85 | 0.66 |  | 38.8 | 21.2 | 0 |  | 323 | 0.04 | 175
2012-12-01 | 0.25 | 0.02 | 0.8 | 0.65 |  | 39.3 | 29 | 0.01 |  | 338 | 0.04 | 203
CY AVG | 0.83 | 0.0175 | 0.82333 | 0.65333 |  | 35.1417 | 28.0333 | 0.00083333 |  | 320.4167 | 0.0375 | 179.75
MAXIMUM | 1.98 | 0.04 | 0.9 | 0.67 |  | 39.3 | 39.3 | 0.01 |  | 349 | 0.04 | 210
MINIMUM | 0.19 | 0 | 0.76 | 0.64 |  | 31.7 | 18.2 | 0 |  | 293 | 0.03 | 149
CEDAR RAPIDS WATER DEPARTMENT
FINISHED WATER ANALYSIS SUMMARY
NW WATER PLANT
CY 2012
[5 empty] | FINISHED WATER HARDNESS LEVELS |  |  |  | ALKALINITY |  | Total |  | Coliform | Sodium
YEAR | p H | Temperature |  |  | mg/L (as CaCO3) |  |  |  | mg/L (as CaCO3) |  | Chlorine | Fluoride | Bacteria
2012 | S.U.'s | Degrees F | Total | Calcium |  | Magnesium | Non-Carb. | Total |  | Phenolpht. | mg/L | mg/l | CFU/100 mL | mg/L
2012-01-01 | 8.2 | 49.2 | 125 | 49 |  | 78 | 67 | 61 |  | 0 | 3.4 | 0.65 | Absent | 13.3
2012-02-01 | 8.24 | 46.1 | 129 | 50 |  | 79 | 69 | 60 |  | 0 | 3.46 | 0.51 | Absent | 14.3
2012-03-01 | 8.24 | 45 | 132 | 48 |  | 84 | 66 | 66 |  | 0 | 3.5 | 0.65 | Absent | 14.9
2012-04-01 | 8.24 | 50.7 | 117 | 43 |  | 74 | 58 | 59 |  | 0 | 3.5 | 0.64 | Absent | 14.2
2012-05-01 | 8.2 | 56 | 116 | 48 |  | 68 | 63 | 53 |  | 0 | 3.4 | 0.62 | Absent | 12.5
2012-06-01 | 8.15 | 63 | 106 | 47 |  | 59 | 60 | 46 |  | 0 | 3.4 | 0.63 | Absent | 11.3
2012-07-01 | 8.16 | 70.1 | 94 | 42 |  | 52 | 48 | 46 |  | 0 | 3.3 | 0.63 | Absent | 12.3
2012-08-01 | 8.19 | 70.8 | 93 | 41 |  | 52 | 42 | 50 |  | 0 | 3.3 | 0.67 | Absent | 14.2
2012-09-01 | 8.23 | 68.9 | 95 | 43 |  | 53 | 44 | 52 |  | 0 | 3.3 | 0.67 | Absent | 16.3
2012-10-01 | 8.2 | 64.7 | 103 | 44 |  | 60 | 46 | 58 |  | 0 | 3.3 | 0.65 | Absent | 17.1
2012-11-01 | 8.21 | 60.7 | 109 | 49 |  | 61 | 51 | 59 |  | 0 | 3.4 | 0.61 | Absent | 18.3
2012-12-01 | 8.17 | 55.3 | 114 | 46 |  | 68 | 57 | 57 |  | 0 | 3.3 | 0.58 | Absent | 17.1
CY AVG | 8.2025 | 58.375 | 111.0833 | 45.8333 |  | 65.6667 | 55.9167 | 55.5833 |  | 0 | 3.38 | 0.62583 | #DIV/0! | 14.65
MAXIMUM | 8.24 | 70.8 | 132 | 50 |  | 84 | 69 | 66 |  | 0 | 3.5 | 0.67 | 0 | 18.3
MINIMUM | 8.15 | 45 | 93 | 41 |  | 52 | 42 | 46 |  | 0 | 3.3 | 0.51 | 0 | 11.3
YEAR | Nitrate | Nitrite | Ammonia | O-Phosphate |  | Chloride | Sulfate | Iron |  | Conductivity | Turbidity | Dissolved
2012 | mg/L (asN) | mg/L (asN) | mg/L (asN) | mg/L (as PO4) |  | mg/L | mg/L as(SO4) | mg/L |  | µmhos/Cm | NTU's | Solids
2012-01-01 | 3.49 | 0 | 0.72 | 0.65 |  | 31.6 | 35.9 | 0 |  | 311 | 0.04 | 186
2012-02-01 | 4.15 | 0 | 0.76 | 0.65 |  | 34.9 | 37.4 | 0 |  | 323 | 0.03 | 182
2012-03-01 | 4.11 | 0 | 0.8 | 0.65 |  | 35 | 37 | 0 |  | 328 | 0.05 | 180
2012-04-01 | 2.87 | 0 | 0.71 | 0.66 |  | 32.3 | 34.5 | 0 |  | 300 | 0.05 | 218
2012-05-01 | 4.99 | 0 | 0.77 | 0.67 |  | 29.7 | 30.7 | 0 |  | 314 | 0.05 | 171
2012-06-01 | 3.79 | 0.01 | 0.69 | 0.66 |  | 29.5 | 30.2 | 0 |  | 291 | 0.05 | 167
2012-07-01 | 1.15 | 0.03 | 0.83 | 0.67 |  | 30.8 | 29.8 | 0 |  | 273 | 0.06 | 155
2012-08-01 | 0.69 | 0.04 | 0.87 | 0.69 |  | 33 | 27.2 | 0 |  | 277 | 0.06 | 142
2012-09-01 | 0.46 | 0.03 | 0.84 | 0.68 |  | 34.8 | 28.6 | 0 |  | 288 | 0.05 | 151
2012-10-01 | 0.4 | 0.04 | 0.86 | 0.69 |  | 36.4 | 30.6 | 0 |  | 305 | 0.06 | 151
2012-11-01 | 0.72 | 0.05 | 0.81 | 0.69 |  | 37.8 | 34.8 | 0 |  | 320 | 0.05 | 176
2012-12-01 | 0.88 | 0.03 | 0.79 | 0.7 |  | 39.5 | 36 | 0 |  | 330 | 0.05 | 206
CY AVG | 2.3083 | 0.019167 | 0.7875 | 0.67167 |  | 33.775 | 32.725 | 0 |  | 305 | 0.05 | 173.75
MAXIMUM | 4.99 | 0.05 | 0.87 | 0.7 |  | 39.5 | 37.4 | 0 |  | 330 | 0.06 | 218
MINIMUM | 0.4 | 0 | 0.69 | 0.65 |  | 29.5 | 27.2 | 0 |  | 273 | 0.03 | 142
Note: ND = Not Detected; recorded as 0.0 for calculation purposes
Note: A= Absent or 0 cfu/100 mL

## CY2013
CEDAR RAPIDS WATER DEPARTMENT
FINISHED WATER ANALYSIS SUMMARY
J AVENUE WATER PLANT
CY 2013
[5 empty] | FINISHED WATER HARDNESS LEVELS |  |  |  | ALKALINITY |  | Total |  | Coliform | Sodium
YEAR | p H | Temperature |  |  | mg/L (as CaCO3) |  |  |  | mg/L (as CaCO3) |  | Chlorine | Fluoride | Bacteria
2013 | S.U.'s | Degrees F | Total | Calcium |  | Magnesium | Non-Carb. | Total |  | Phenolpht. | mg/L | mg/L | CFU/100 mL | mg/L
2013-01-01 | 8.17 | 60.9 | 126 | 62 |  | 64 | 49 | 77 |  | 0 | 3.3 | 0.48 | Absent | 20.2
2013-02-01 | 8.2 | 56.5 | 136 | 67 |  | 70 | 59 | 78 |  | 0 | 3.4 | 0.46 | Absent | 20.7
2013-03-01 | 8.2 | 52.8 | 141 | 71 |  | 70 | 58 | 84 |  | 0 | 3.3 | 0.46 | Absent | 18.6
2013-04-01 | 8.19 | 50.1 | 129 | 71 |  | 59 | 54 | 75 |  | 0 | 3.2 | 0.53 | Absent | 15.5
2013-05-01 | 8.19 | 52.2 | 134 | 73 |  | 61 | 69 | 64 |  | 0 | 3.3 | 0.61 | Absent | 11.6
2013-06-01 | 8.18 | 59.9 | 120 | 64 |  | 56 | 64 | 56 |  | 0 | 3.2 | 0.56 | Absent | 9.96
2013-07-01 | 8.28 | 65.7 | 113 | 60 |  | 54 | 58 | 55 |  | 0 | 3.2 | 0.17 | Absent | 8.9
2013-08-01 | 8.25 | 68.1 | 112 | 58 |  | 53 | 58 | 54 |  | 0 | 3.2 | 0.17 | Absent | 10.3
2013-09-01 | 8.29 | 69 | 109 | 58 |  | 52 | 54 | 56 |  | 0 | 3.3 | 0.19 | Absent | 11.9
2013-10-01
2013-11-01
2013-12-01
CY AVG | 8.2167 | 59.4667 | 124.4444 | 64.8889 |  | 59.8889 | 58.1111 | 66.5556 |  | 0 | 3.2667 | 0.40333 | #DIV/0! | 14.1844
MAXIMUM | 8.29 | 69 | 141 | 73 |  | 70 | 69 | 84 |  | 0 | 3.4 | 0.61 | 0 | 20.7
MINIMUM | 8.17 | 50.1 | 109 | 58 |  | 52 | 49 | 54 |  | 0 | 3.2 | 0.17 | 0 | 8.9
EPA MCL | [10 empty] | 4 | 4 | 0
Reg. Min. | 8.0-8.4 | [9 empty] | 1.5
2nd NEG | [11 empty] | 2
OPS |  | OPS | OPS | OPS |  | OPS | OPS | OPS |  | OPS
NR | [13 empty] | NR
Note: MCL = Maximum Contaminant Level; OPS = Operational Parameter; Reg. Min. = Regulatory Minimum; 2nd NEG=Secondary Nonenforceable Guideline; NR = Not Regulated
YEAR | Nitrate | Nitrite | Ammonia | O-Phosphate |  | Chloride | Sulfate | Iron |  | Conductivity | Turbidity | Dissolved
2013 | mg/L (asN) | mg/L (asN) | mg/L (asN) | mg/L (as PO4) |  | mg/L | mg/L as(SO4) | mg/L |  | µmhos/Cm | NTU's | Solids
2013-01-01 | 0.27 | 0.03 | 0.88 | 0.64 |  | 41.1 | 32.6 | 0 |  | 356 | 0.04 | 204
2013-02-01 | 0.38 | 0.03 | 1.03 | 0.65 |  | 45.2 | 40.3 | 0 |  | 385 | 0.04 | 242
2013-03-01 | 0.69 | 0.04 | 1.09 | 0.65 |  | 42.8 | 39.1 | 0 |  | 389 | 0.04 | 233
2013-04-01 | 1.48 | 0.02 | 0.76 | 0.68 |  | 34.8 | 34 | 0 |  | 350 | 0.05 | 214
2013-05-01 | 5.03 | 0.04 | 0.85 | 0.67 |  | 31.8 | 32.8 | 0 |  | 350 | 0.05 | 204
2013-06-01 | 5.67 | 0.04 | 0.78 | 0.66 |  | 28.3 | 27.6 | 0 |  | 317 | 0.05 | 194
2013-07-01 | 4.32 | 0.04 | 0.76 | 0.66 |  | 26.4 | 28.3 | 0 |  | 297 | 0.04 | 198
2013-08-01 | 2.96 | 0.03 | 0.8 | 0.68 |  | 27.8 | 32.3 | 0 |  | 297 | 0.04 | 177
2013-09-01 | 0.98 | 0.03 | 0.81 | 0.65 |  | 30.3 | 34.5 | 0 |  | 297 | 0.05 | 184
2013-10-01
2013-11-01
2013-12-01
CY AVG | 2.42 | 0.033333 | 0.86222 | 0.66 |  | 34.2778 | 33.5 | 0 |  | 337.5556 | 0.044444 | 205.5556
MAXIMUM | 5.67 | 0.04 | 1.09 | 0.68 |  | 45.2 | 40.3 | 0 |  | 389 | 0.05 | 242
MINIMUM | 0.27 | 0.02 | 0.76 | 0.64 |  | 26.4 | 27.6 | 0 |  | 297 | 0.04 | 177
EPA MCL | 10 | 1 | [8 empty] | 0.3
Reg. Min.
2nd NEG | [5 empty] | 250 | 250 | 0.3 |  |  |  | 500
OPS |  |  | OPS | OPS | [5 empty] | OPS
Note: MCL = Maximum Contaminant Level; OPS = Operational Parameter; Reg. Min. = Regulatory Minimum; 2nd NEG=Secondary Nonenforceable Guideline; NR = Not Regulated
CEDAR RAPIDS WATER DEPARTMENT
FINISHED WATER ANALYSIS SUMMARY
NW WATER PLANT
CY 2013
[5 empty] | FINISHED WATER HARDNESS LEVELS |  |  |  | ALKALINITY |  | Total |  | Coliform | Sodium
YEAR | p H | Temperature |  |  | mg/L (as CaCO3) |  |  |  | mg/L (as CaCO3) |  | Chlorine | Fluoride | Bacteria
2013 | S.U.'s | Degrees F | Total | Calcium |  | Magnesium | Non-Carb. | Total |  | Phenolpht. | mg/L | mg/l | CFU/100 mL | mg/L
2013-01-01 | 8.18 | 53.7 | 118 | 44 |  | 73 | 62 | 56 |  | 0 | 3.2 | 0.54 | Absent | 20.3
2013-02-01 | 8.15 | 49.9 | 124 | 49 |  | 75 | 70 | 54 |  | 0 | 3.4 | 0.5 | Absent | 21.7
2013-03-01 | 8.15 | 48.8 | 122 | 47 |  | 75 | 67 | 55 |  | 0 | 3.4 | 0.54 | Absent | 18.5
2013-04-01 | 8.15 | 47.1 | 121 | 52 |  | 69 | 64 | 57 |  | 0 | 3.4 | 0.55 | Absent | 17.1
2013-05-01 | 8.09 | 50.1 | 121 | 54 |  | 66 | 75 | 46 |  | 0 | 3.4 | 0.56 | Absent | 11.7
2013-06-01 | 8.22 | 56.4 | 111 | 48 |  | 63 | 66 | 45 |  | 0 | 3.4 | 0.56 | Absent | 9.5
2013-07-01 | 8.27 | 62.3 | 107 | 47 |  | 60 | 60 | 47 |  | 0 | 3.4 | 0.16 | Absent | 9
2013-08-01 | 8.27 | 65.8 | 109 | 48 |  | 60 | 62 | 47 |  | 0 | 3.4 | 0.16 | Absent | 10.9
2013-09-01 | 8.29 | 69.3 | 105 | 49 |  | 56 | 59 | 46 |  | 0 | 3.4 | 0.18 | Absent | 11.7
2013-10-01
2013-11-01
2013-12-01
CY AVG | 8.1967 | 55.9333 | 115.3333 | 48.6667 |  | 66.3333 | 65 | 50.3333 |  | 0 | 3.3778 | 0.41667 | #DIV/0! | 14.4889
MAXIMUM | 8.29 | 69.3 | 124 | 54 |  | 75 | 75 | 57 |  | 0 | 3.4 | 0.56 | 0 | 21.7
MINIMUM | 8.09 | 47.1 | 105 | 44 |  | 56 | 59 | 45 |  | 0 | 3.2 | 0.16 | 0 | 9
EPA MCL | [10 empty] | 4 | 4 | 0
Reg. Min. | 8.0-8.4 | [9 empty] | 1.5
2nd NEG | [11 empty] | 2
OPS |  | OPS | OPS | OPS |  | OPS | OPS | OPS |  | OPS
NR | [13 empty] | NR
Note: MCL = Maximum Contaminant Level; OPS = Operational Parameter; Reg. Min. = Regulatory Minimum; 2nd NEG=Secondary Nonenforceable Guideline; NR = Not Regulated
YEAR | Nitrate | Nitrite | Ammonia | O-Phosphate |  | Chloride | Sulfate | Iron |  | Conductivity | Turbidity | Dissolved
2013 | mg/L (asN) | mg/L (asN) | mg/L (asN) | mg/L (as PO4) |  | mg/L | mg/L as(SO4) | mg/L |  | µmhos/Cm | NTU's | Solids
2013-01-01 | 1.06 | 0.03 | 0.83 | 0.66 |  | 40.4 | 42.4 | 0.01 |  | 344 | 0.05 | 200
2013-02-01 | 2.03 | 0.03 | 0.89 | 0.66 |  | 44.6 | 46.3 | 0 |  | 367 | 0.05 | 220
2013-03-01 | 2.26 | 0.03 | 0.8 | 0.66 |  | 39.1 | 44.8 | 0 |  | 355 | 0.06 | 207
2013-04-01 | 2.53 | 0.03 | 0.88 | 0.7 |  | 34.6 | 41.2 | 0 |  | 338 | 0.05 | 198
2013-05-01 | 6.37 | 0.03 | 0.78 | 0.66 |  | 31 | 35.6 | 0 |  | 327 | 0.06 | 187
2013-06-01 | 6.64 | 0.03 | 0.73 | 0.67 |  | 26 | 28.3 | 0 |  | 294 | 0.07 | 173
2013-07-01 | 4.91 | 0.04 | 0.8 | 0.67 |  | 25.3 | 28.8 | 0 |  | 283 | 0.06 | 187
2013-08-01 | 4.2 | 0.02 | 0.83 | 0.67 |  | 27.3 | 33.5 | 0 |  | 294 | 0.05 | 171
2013-09-01 | 1.99 | 0.04 | 0.84 | 0.66 |  | 29.5 | 37.6 | 0 |  | 290 | 0.06 | 191
2013-10-01
2013-11-01
2013-12-01
CY AVG | 3.5544 | 0.031111 | 0.82 | 0.66778 |  | 33.0889 | 37.6111 | 0.0011111 |  | 321.3333 | 0.056667 | 192.6667
MAXIMUM | 6.64 | 0.04 | 0.89 | 0.7 |  | 44.6 | 46.3 | 0.01 |  | 367 | 0.07 | 220
MINIMUM | 1.06 | 0.02 | 0.73 | 0.66 |  | 25.3 | 28.3 | 0 |  | 283 | 0.05 | 171
EPA MCL | 10 | 1 | [8 empty] | 0.3
Reg. Min.
2nd NEG | [5 empty] | 250 | 250 | 0.3 |  |  |  | 500
OPS |  |  | OPS | OPS | [5 empty] | OPS
Note: MCL = Maximum Contaminant Level; OPS = Operational Parameter; Reg. Min. = Regulatory Minimum; 2nd NEG=Secondary Nonenforceable Guideline; NR = Not Regulated

## CY2014
CEDAR RAPIDS WATER DEPARTMENT
FINISHED WATER ANALYSIS SUMMARY
J AVENUE WATER PLANT
CY 2014
[5 empty] | FINISHED WATER HARDNESS LEVELS |  |  |  | ALKALINITY |  | Total |  | Coliform | Sodium
YEAR | p H | Temperature |  |  | mg/L (as CaCO3) |  |  |  | mg/L (as CaCO3) |  | Chlorine | Fluoride | Bacteria
2014 | S.U.'s | Degrees F | Total | Calcium |  | Magnesium | Non-Carb. | Total |  | Phenolpht. | mg/L | mg/L | CFU/100 mL | mg/L
2014-01-01
2014-02-01
2014-03-01
2014-04-01
2014-05-01
2014-06-01
2014-07-01
2014-08-01
2014-09-01
2014-10-01
2014-11-01
2014-12-01
CY AVG | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
MAXIMUM | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
MINIMUM | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
EPA MCL | [10 empty] | 4 | 4 | 0
Reg. Min. | 8.0-8.4 | [9 empty] | 1.5
2nd NEG | [11 empty] | 2
OPS |  | OPS | OPS | OPS |  | OPS | OPS | OPS |  | OPS
NR | [13 empty] | NR
Note: MCL = Maximum Contaminant Level; OPS = Operational Parameter; Reg. Min. = Regulatory Minimum; 2nd NEG=Secondary Nonenforceable Guideline; NR = Not Regulated
YEAR | Nitrate | Nitrite | Ammonia | O-Phosphate |  | Chloride | Sulfate | Iron |  | Conductivity | Turbidity | Dissolved
2014 | mg/L (asN) | mg/L (asN) | mg/L (asN) | mg/L (as PO4) |  | mg/L | mg/L as(SO4) | mg/L |  | µmhos/Cm | NTU's | Solids
2014-01-01
2014-02-01
2014-03-01
2014-04-01
2014-05-01
2014-06-01
2014-07-01
2014-08-01
2014-09-01
2014-10-01
2014-11-01
2014-12-01
CY AVG | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0!
MAXIMUM | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
MINIMUM | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
EPA MCL | 10 | 1 | [8 empty] | 0.3
Reg. Min.
2nd NEG | [5 empty] | 250 | 250 | 0.3 |  |  |  | 500
OPS |  |  | OPS | OPS | [5 empty] | OPS
Note: MCL = Maximum Contaminant Level; OPS = Operational Parameter; Reg. Min. = Regulatory Minimum; 2nd NEG=Secondary Nonenforceable Guideline; NR = Not Regulated
CEDAR RAPIDS WATER DEPARTMENT
FINISHED WATER ANALYSIS SUMMARY
NW WATER PLANT
CY 2014
[5 empty] | FINISHED WATER HARDNESS LEVELS |  |  |  | ALKALINITY |  | Total |  | Coliform | Sodium
YEAR | p H | Temperature |  |  | mg/L (as CaCO3) |  |  |  | mg/L (as CaCO3) |  | Chlorine | Fluoride | Bacteria
2014 | S.U.'s | Degrees F | Total | Calcium |  | Magnesium | Non-Carb. | Total |  | Phenolpht. | mg/L | mg/l | CFU/100 mL | mg/L
2014-01-01
2014-02-01
2014-03-01
2014-04-01
2014-05-01
2014-06-01
2014-07-01
2014-08-01
2014-09-01
2014-10-01
2014-11-01
2014-12-01
CY AVG | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
MAXIMUM | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
MINIMUM | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
EPA MCL | [10 empty] | 4 | 4 | 0
Reg. Min. | 8.0-8.4 | [9 empty] | 1.5
2nd NEG | [11 empty] | 2
OPS |  | OPS | OPS | OPS |  | OPS | OPS | OPS |  | OPS
NR | [13 empty] | NR
Note: MCL = Maximum Contaminant Level; OPS = Operational Parameter; Reg. Min. = Regulatory Minimum; 2nd NEG=Secondary Nonenforceable Guideline; NR = Not Regulated
YEAR | Nitrate | Nitrite | Ammonia | O-Phosphate |  | Chloride | Sulfate | Iron |  | Conductivity | Turbidity | Dissolved
2014 | mg/L (asN) | mg/L (asN) | mg/L (asN) | mg/L (as PO4) |  | mg/L | mg/L as(SO4) | mg/L |  | µmhos/Cm | NTU's | Solids
2014-01-01
2014-02-01
2014-03-01
2014-04-01
2014-05-01
2014-06-01
2014-07-01
2014-08-01
2014-09-01
2014-10-01
2014-11-01
2014-12-01
CY AVG | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0!
MAXIMUM | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
MINIMUM | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
EPA MCL | 10 | 1 | [8 empty] | 0.3
Reg. Min.
2nd NEG | [5 empty] | 250 | 250 | 0.3 |  |  |  | 500
OPS |  |  | OPS | OPS | [5 empty] | OPS
Note: MCL = Maximum Contaminant Level; OPS = Operational Parameter; Reg. Min. = Regulatory Minimum; 2nd NEG=Secondary Nonenforceable Guideline; NR = Not Regulated